## Tabelle1
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14 | Column15 | Column16 | Column17 | Column18 | Column19 | Column20 | Column21 | Column22 | Column23 | Column24 | Column25 | Column26 | Column27 | Column28 | Column29 | Column30 | Column31 | Column32 | Column33 | ttd_l evap
| GKM_00AQC10CE006_XP20:A | GKM_B1CJU10DT915_XQ70:A | GKM_B1CJU10FQ910_XQ01:A | GKM_B1HPD10CL001_XQ01:A | GKM_B1HPD10FP901_XQ01:A | GKM_B1HPD10FT901_XQ01:A | GKM_B1HPD10FT903_XQ01:A | GKM_B1HPE10CP002_XQ01:A | GKM_B1HPE10CT005_XQ01:A | GKM_B1HPE10CT006_XQ01:A | GKM_B1HPE15AA101_XQ01:A | GKM_B1HPE20AA101_XQ01:A | GKM_B1HPE20CL001_XQ01:A | GKM_B1HPE20CL002_XQ01:A | GKM_B1HPE20CT001_XQ01:A | GKM_B1HPE30AA101_XQ01:A | GKM_B1HPE30CL001_XQ01:A | GKM_B1HPE30CP001_XQ01:A | GKM_B1HPW10CP002_XQ01:A | GKM_B1MLA10AN001_XB01:B | GKM_B1MLA10CE004_XQ01:A | GKM_B1NDA10CT001_XQ01:A | GKM_B1NDB40CT001_XQ01:A | GKM_B1NDB40FF901_XQ01:A | GKM_B1PAB10CF001_XQ01:A | GKM_B1PAB30CT901_XQ01:A | GKM_B1PAB40CT901_XQ01:A |  |  | #SYNTAX |  |  | #SYNTAX
Description | Total electrical power WPA1 | Soll-Wert FernHzWa Temp WPA1 akt | Power factor WPA1 | L(evel) evaporator /vapour ratio x | Pressure in the evaporator | Temperature in the evaporator | T Compressor overheating | P 2hi compressor | T Verdi Stufe 1 | T hi Compressor | RV Bypass Condensor ? | RV HD Niveau Kondensator | L Kondensator | L Subcooling Template | T behind subcooler | RV ND Niveau ZwischenBeh | L ZwischenBeh | P ZwischenBeh | DP Sealing oil/refrigerant | Motor Verdichter An/Aus WP1 | Motor power compressor WP1 | T Remote heating behind WPA1 / temp supplied from hp? | Temp. return to heatpump ? | Mass flow rate return to heating n/w | Volume flow rate input | Source input temp ? | Source out temp ? | Mass flow rate at sink | Qdot at condensor | #SYNTAX | COP calculated | Temp difference | #SYNTAX
Displayname | GKM-GEN--MEA-POW-EL---HP------EL-- | GKM-GEN--SET-T----HP------W-H- | GKM-GEN--MEA-KPI----HP-------- | GKM-GEN--MEA-LEV----HP--EVAP----REF-R1234- | GKM-GEN--MEA-P----HP--EVAP----REF-R1234- | GKM-GEN--MEA-T----HP--EVAP----REF-R1234- | GKM-GEN--MEA-T-SHE-IN--HP--COMP-1---REF-R1234- | GKM-GEN--MEA-P--OUT--HP--COMP-2---REF-R1234- | GKM-GEN--MEA-T--OUT--HP--COMP-1---REF-R1234- | GKM-GEN--MEA-T--OUT--HP--COMP-2---REF-R1234- | GKM-GEN--MEA-POS----HP--COND--VAL-BY-REF-R1234- | GKM-GEN--MEA-POS----HP--COND--VAL--REF-R1234- | GKM-GEN--MEA-LEV----HP--COND----REF-R1234- | GKM-GEN--MEA-LEV----HP--SUBC----REF-R1234- | GKM-GEN--MEA-T--OUT--HP--SUBC----REF-R1234- | GKM-GEN--MEA-POS----HP--FT--VAL--REF-R1234- | GKM-GEN--MEA-LEV----HP--FT----REF-R1234- | GKM-GEN--MEA-P----HP--FT----REF-R1234- | GKM-GEN--MEA-P-DIF---HP------OIL-- | GKM-GEN--STAT-ON----HP--COMP------ | GKM-GEN--MEA-POW-EL---HP--COMP----EL-- | GKM-TRNS--MEA-T--SUP--HP------W-H- | GKM-TRNS--MEA-T--RET-2-HP------W-H- | GKM-TRNS--MEA-MF--RET--HP------W-H- | GKM-SRC--MEA-VF--IN--HP------W-R- | GKM-SRC--MEA-T--IN--HP------W-R- | GKM-SRC--MEA-T--OUT--HP------W-R- |  |  | #SYNTAX | Qdot/Motor power |  | #SYNTAX
Unit | kW | °C | - | % | bara | °C | °C | bara | °C | °C | % | % | % | % | °C | % | % | bara | bara | 0/1 | kW | °C | °C | t/h | m³/h | °C | °C | kg/s | MW | #SYNTAX |  |  | #SYNTAX
2024-12-15 | 6482.65 | 99 | 2.63 | 25.58 | 2.16 | -0.08 | -1.57 | 28.62 | -1.68 | 104.31 | 0.47 | 16.7 | 54.84 | 103.14 | 64.5 | 27.07 | 33.96 | 8.62 | 2.71 | 1 | 6040.91 | 97.12 | 60.38 | 369.07 | 2530.99 | 7.01 | 3.7 | 102.52 | 15.74 | 3.31 | 2.61 | 90.11 | 3.78
2024-12-15 00:15 | 6469.4 | 99 | 2.61 | 25.26 | 2.16 | 0.1 | -1.59 | 28.78 | -1.5 | 104.35 | 0.47 | 16.87 | 55.04 | 103.14 | 64.5 | 27.16 | 34.12 | 8.62 | 2.71 | 1 | 6104.99 | 97.14 | 60.39 | 368.15 | 2522.36 | 7.24 | 3.91 | 102.26 | 15.71 | 3.33 | 2.57 | 104.25 | 3.81
2024-12-15 00:30 | 6484.75 | 99 | 2.6 | 25.35 | 2.16 | -0.08 | -1.52 | 28.82 | -1.5 | 104.39 | 0.47 | 16.7 | 54.8 | 103.14 | 64.49 | 27.2 | 33.99 | 8.62 | 2.71 | 1 | 6096.62 | 97.15 | 60.41 | 367.22 | 2522.5 | 7.15 | 3.82 | 102.01 | 15.67 | 3.33 | 2.57 | 104.47 | 3.9
2024-12-15 00:45 | 6475.25 | 99 | 2.61 | 24.99 | 2.16 | -0.04 | -1.45 | 28.84 | -1.47 | 104.43 | 0.47 | 16.74 | 54.96 | 103.14 | 64.48 | 27.05 | 34.13 | 8.61 | 2.71 | 1 | 6070.18 | 97.16 | 60.43 | 364.79 | 2525.76 | 7.14 | 3.81 | 101.33 | 15.56 | 3.33 | 2.56 | 104.47 | 3.85
2024-12-15 01:00 | 6485 | 99 | 2.59 | 25.11 | 2.16 | -0.05 | -1.47 | 28.77 | -1.55 | 104.47 | 0.47 | 16.69 | 54.98 | 103.14 | 64.47 | 27.03 | 34.04 | 8.61 | 2.71 | 1 | 6075.66 | 97.18 | 60.45 | 367.78 | 2534.48 | 7.07 | 3.73 | 102.16 | 15.68 | 3.34 | 2.58 | 104.52 | 3.78
2024-12-15 01:15 | 6485 | 99 | 2.61 | 25.41 | 2.16 | -0.07 | -1.62 | 28.81 | -1.73 | 104.51 | 0.47 | 16.75 | 54.94 | 103.14 | 64.46 | 27.2 | 33.88 | 8.61 | 2.71 | 1 | 6074.66 | 97.19 | 60.46 | 368.56 | 2516 | 7.01 | 3.7 | 102.38 | 15.72 | 3.31 | 2.59 | 104.58 | 3.77
2024-12-15 01:30 | 6485.07 | 99 | 2.6 | 25.04 | 2.16 | -0.05 | -1.48 | 28.8 | -1.7 | 104.55 | 0.47 | 16.82 | 55 | 103.14 | 64.45 | 27.17 | 34.06 | 8.61 | 2.71 | 1 | 6093.29 | 97.2 | 60.48 | 369.34 | 2510.92 | 7.04 | 3.72 | 102.59 | 15.75 | 3.32 | 2.58 | 104.6 | 3.77
2024-12-15 01:45 | 6488.05 | 99 | 2.58 | 25.3 | 2.16 | -0.06 | -1.59 | 28.79 | -1.67 | 104.59 | 0.47 | 16.63 | 54.93 | 103.14 | 64.44 | 27.05 | 34.05 | 8.61 | 2.71 | 1 | 6099.85 | 97.22 | 60.5 | 370.12 | 2526.77 | 7.06 | 3.73 | 102.81 | 15.78 | 3.33 | 2.59 | 104.65 | 3.79
2024-12-15 02:00 | 6489.83 | 99 | 2.61 | 25.21 | 2.16 | -0.06 | -1.62 | 28.84 | -1.71 | 104.63 | 0.47 | 16.65 | 54.85 | 103.14 | 64.43 | 26.96 | 34 | 8.61 | 2.71 | 1 | 6078.54 | 97.23 | 60.51 | 370.9 | 2531.87 | 7.08 | 3.75 | 103.03 | 15.81 | 3.33 | 2.6 | 104.69 | 3.81
2024-12-15 02:15 | 6483.12 | 99 | 2.61 | 25.22 | 2.16 | 0 | -1.69 | 28.83 | -1.68 | 104.67 | 0.47 | 16.79 | 54.95 | 103.14 | 64.42 | 26.96 | 33.83 | 8.61 | 2.71 | 1 | 6082.76 | 97.24 | 60.53 | 371.5 | 2505.83 | 7.12 | 3.81 | 103.19 | 15.83 | 3.31 | 2.6 | 104.67 | 3.81
2024-12-15 02:30 | 6488.68 | 99 | 2.6 | 25.01 | 2.16 | 0.07 | -1.7 | 28.92 | -1.65 | 104.71 | 0.47 | 16.92 | 55.14 | 103.14 | 64.41 | 26.93 | 34.09 | 8.62 | 2.71 | 1 | 6109.61 | 97.26 | 60.55 | 371.33 | 2523.95 | 7.26 | 3.91 | 103.15 | 15.83 | 3.35 | 2.59 | 104.64 | 3.84
2024-12-15 02:45 | 6514.65 | 99 | 2.58 | 25.09 | 2.16 | 0 | -1.35 | 28.92 | -1.5 | 104.75 | 0.47 | 16.77 | 55.03 | 103.14 | 64.4 | 27.14 | 34.28 | 8.62 | 2.71 | 1 | 6109.47 | 97.27 | 60.56 | 371.16 | 2539.06 | 7.07 | 3.76 | 103.1 | 15.82 | 3.31 | 2.59 | 104.75 | 3.76
2024-12-15 03:00 | 6500.67 | 99 | 2.59 | 25.24 | 2.16 | -0.02 | -1.47 | 28.87 | -1.46 | 104.79 | 0.47 | 16.78 | 54.91 | 103.14 | 64.39 | 27.18 | 34.14 | 8.63 | 2.71 | 1 | 6075.65 | 97.28 | 60.58 | 370.99 | 2514.2 | 7.05 | 3.77 | 103.05 | 15.81 | 3.28 | 2.6 | 104.81 | 3.79
2024-12-15 03:15 | 6488.25 | 99 | 2.61 | 25.13 | 2.16 | -0.01 | -1.68 | 28.97 | -1.7 | 104.83 | 0.46 | 16.83 | 55.06 | 103.14 | 64.38 | 26.87 | 34.1 | 8.63 | 2.71 | 1 | 6093.24 | 97.3 | 60.6 | 370.82 | 2518.81 | 7.06 | 3.77 | 103.01 | 15.8 | 3.29 | 2.59 | 104.84 | 3.78
2024-12-15 03:30 | 6497.9 | 99 | 2.6 | 25.27 | 2.16 | 0.06 | -1.61 | 29 | -1.61 | 104.87 | 0.46 | 16.86 | 55.04 | 103.14 | 64.37 | 27.02 | 34.09 | 8.64 | 2.71 | 1 | 6103.34 | 97.31 | 60.61 | 370.65 | 2525.64 | 7.08 | 3.79 | 102.96 | 15.79 | 3.29 | 2.59 | 104.81 | 3.73
2024-12-15 03:45 | 6494.3 | 99 | 2.59 | 25.44 | 2.16 | 0.01 | -1.47 | 29.02 | -1.43 | 104.91 | 0.46 | 16.73 | 54.97 | 103.14 | 64.36 | 27.07 | 33.9 | 8.64 | 2.71 | 1 | 6104.45 | 97.32 | 60.63 | 370.48 | 2536.32 | 7.13 | 3.83 | 102.91 | 15.78 | 3.3 | 2.59 | 104.9 | 3.82
2024-12-15 04:00 | 6505.7 | 99 | 2.6 | 25.5 | 2.16 | -0.02 | -1.59 | 29.04 | -1.61 | 104.95 | 0.46 | 16.87 | 54.99 | 103.14 | 64.35 | 27.04 | 33.81 | 8.65 | 2.71 | 1 | 6115.45 | 97.34 | 60.64 | 370.31 | 2506.33 | 7.14 | 3.82 | 102.86 | 15.78 | 3.32 | 2.58 | 104.97 | 3.84
2024-12-15 04:15 | 6494.25 | 99 | 2.59 | 25.09 | 2.16 | -0.02 | -1.4 | 29.01 | -1.5 | 104.99 | 0.46 | 16.83 | 55.04 | 103.14 | 64.34 | 26.94 | 34.22 | 8.65 | 2.71 | 1 | 6115.5 | 97.35 | 60.64 | 370.14 | 2521.55 | 7.18 | 3.84 | 102.82 | 15.78 | 3.34 | 2.58 | 105.01 | 3.86
2024-12-15 04:30 | 6504.05 | 99 | 2.6 | 25.32 | 2.16 | -0.02 | -1.48 | 29.05 | -1.39 | 105.03 | 0.46 | 16.84 | 54.95 | 103.14 | 64.33 | 26.69 | 33.96 | 8.65 | 2.71 | 1 | 6085.48 | 97.36 | 60.64 | 369.97 | 2509.28 | 7.09 | 3.78 | 102.77 | 15.77 | 3.31 | 2.59 | 105.05 | 3.8
2024-12-15 04:45 | 6506.3 | 99 | 2.58 | 25.36 | 2.16 | -0.01 | -1.54 | 29.1 | -1.6 | 105.06 | 0.46 | 16.73 | 55.01 | 103.14 | 64.32 | 26.56 | 33.84 | 8.66 | 2.71 | 1 | 6090.98 | 97.37 | 60.64 | 369.8 | 2506.11 | 7.02 | 3.7 | 102.72 | 15.77 | 3.32 | 2.59 | 105.07 | 3.71
2024-12-15 05:00 | 6517.5 | 99 | 2.61 | 25.59 | 2.16 | -0.01 | -1.37 | 29.1 | -1.4 | 105.1 | 0.46 | 16.59 | 55.02 | 103.14 | 64.31 | 26.83 | 33.87 | 8.66 | 2.71 | 1 | 6104.6 | 97.39 | 60.64 | 369.63 | 2520.51 | 7.01 | 3.73 | 102.68 | 15.77 | 3.28 | 2.58 | 105.11 | 3.74
2024-12-15 05:15 | 6497.9 | 99 | 2.58 | 25.66 | 2.16 | -0.04 | -1.52 | 29.06 | -1.57 | 105.07 | 0.46 | 16.76 | 55.02 | 103.14 | 64.3 | 26.57 | 33.69 | 8.67 | 2.71 | 1 | 6069.91 | 97.4 | 60.64 | 369.46 | 2498.01 | 6.95 | 3.67 | 102.63 | 15.77 | 3.28 | 2.6 | 105.11 | 3.71
2024-12-15 05:30 | 6494 | 99 | 2.57 | 25.79 | 2.16 | -0.08 | -1.48 | 29.08 | -1.6 | 105.05 | 0.46 | 16.72 | 54.9 | 103.14 | 64.29 | 26.77 | 33.79 | 8.67 | 2.71 | 1 | 6085.33 | 97.41 | 60.64 | 369.29 | 2506.01 | 6.94 | 3.63 | 102.58 | 15.77 | 3.31 | 2.59 | 105.13 | 3.71
2024-12-15 05:45 | 6494.05 | 99 | 2.59 | 25.52 | 2.16 | -0.11 | -1.52 | 29.12 | -1.65 | 105.03 | 0.46 | 16.7 | 55.06 | 103.14 | 64.28 | 26.34 | 33.71 | 8.68 | 2.71 | 1 | 6086.53 | 97.41 | 60.64 | 369.12 | 2536.77 | 6.93 | 3.67 | 102.53 | 15.76 | 3.26 | 2.59 | 105.14 | 3.78
2024-12-15 06:00 | 6496.07 | 99 | 2.58 | 25.46 | 2.16 | -0.03 | -1.32 | 29.2 | -1.45 | 105.01 | 0.46 | 16.69 | 55.06 | 103.14 | 64.28 | 26.79 | 33.81 | 8.68 | 2.71 | 1 | 6116.94 | 97.39 | 60.65 | 368.95 | 2517.73 | 6.96 | 3.69 | 102.49 | 15.74 | 3.27 | 2.57 | 105.04 | 3.72
2024-12-15 06:15 | 6498.97 | 99 | 2.59 | 25.81 | 2.16 | -0.02 | -1.31 | 29.17 | -1.4 | 104.98 | 0.46 | 16.65 | 55.11 | 103.14 | 64.27 | 26.77 | 33.51 | 8.69 | 2.71 | 1 | 6094.69 | 97.36 | 60.65 | 368.78 | 2515.78 | 7.02 | 3.75 | 102.44 | 15.72 | 3.27 | 2.58 | 105 | 3.77
2024-12-15 06:30 | 6498.22 | 99 | 2.58 | 25.64 | 2.16 | 0 | -1.28 | 29.19 | -1.3 | 104.96 | 0.46 | 16.75 | 55.05 | 103.14 | 64.26 | 26.62 | 33.6 | 8.69 | 2.72 | 1 | 6081.63 | 97.34 | 60.65 | 366.93 | 2515.32 | 7 | 3.76 | 101.93 | 15.63 | 3.24 | 2.57 | 104.96 | 3.76
2024-12-15 06:45 | 6506.73 | 99 | 2.58 | 25.52 | 2.16 | 0 | -1.5 | 29.27 | -1.38 | 104.94 | 0.46 | 16.61 | 55.01 | 103.14 | 64.25 | 26.77 | 33.62 | 8.7 | 2.72 | 1 | 6100.64 | 97.32 | 60.65 | 362.89 | 2519.4 | 7.04 | 3.74 | 100.8 | 15.45 | 3.3 | 2.53 | 104.94 | 3.74
2024-12-15 07:00 | 6495.87 | 99 | 2.59 | 25.78 | 2.16 | -0.05 | -1.64 | 29.15 | -1.7 | 104.91 | 0.46 | 16.61 | 54.96 | 103.14 | 64.24 | 26.59 | 33.76 | 8.65 | 2.72 | 1 | 6084.3 | 97.29 | 60.65 | 373.76 | 2500.44 | 6.92 | 3.65 | 103.82 | 15.9 | 3.27 | 2.61 | 104.96 | 3.7
2024-12-15 07:15 | 6489 | 99 | 2.62 | 25.49 | 2.16 | -0.1 | -1.53 | 28.78 | -1.71 | 104.38 | 0.46 | 16.64 | 54.96 | 103.14 | 64.23 | 26.8 | 33.8 | 8.6 | 2.72 | 1 | 6046.73 | 97.27 | 60.65 | 373.61 | 2526.1 | 6.9 | 3.63 | 103.78 | 15.89 | 3.27 | 2.63 | 104.48 | 3.73
2024-12-15 07:30 | 6409.92 | 99 | 2.63 | 26.26 | 2.16 | -0.08 | -1.35 | 28.43 | -1.5 | 103.2 | 0.45 | 16.62 | 54.72 | 103.14 | 64.22 | 26.95 | 33.59 | 8.53 | 2.72 | 1 | 5957.87 | 97.25 | 60.65 | 373.45 | 2512.73 | 6.91 | 3.62 | 103.74 | 15.87 | 3.29 | 2.66 | 103.28 | 3.7
2024-12-15 07:45 | 6367.55 | 99 | 2.63 | 26.21 | 2.16 | -0.09 | -1.5 | 28.43 | -1.59 | 103.19 | 0.45 | 16.59 | 54.76 | 103.14 | 64.21 | 26.88 | 33.35 | 8.51 | 2.72 | 1 | 5943.92 | 97.22 | 60.65 | 373.3 | 2519.69 | 6.91 | 3.63 | 103.69 | 15.85 | 3.28 | 2.67 | 103.28 | 3.72
2024-12-15 08:00 | 6350.45 | 99 | 2.62 | 26.12 | 2.16 | -0.12 | -1.52 | 28.38 | -1.6 | 103.18 | 0.45 | 16.61 | 54.85 | 103.14 | 64.21 | 26.73 | 33.35 | 8.51 | 2.72 | 1 | 5950.92 | 97.2 | 60.65 | 373.14 | 2506.74 | 6.98 | 3.69 | 103.65 | 15.84 | 3.29 | 2.66 | 103.3 | 3.81
2024-12-15 08:15 | 6367.93 | 99 | 2.62 | 26.63 | 2.16 | -0.14 | -1.42 | 28.41 | -1.5 | 103.17 | 0.45 | 16.53 | 54.68 | 103.14 | 64.25 | 26.88 | 32.98 | 8.51 | 2.72 | 1 | 5936.09 | 97.17 | 60.65 | 372.99 | 2518.85 | 6.9 | 3.62 | 103.61 | 15.82 | 3.28 | 2.66 | 103.31 | 3.76
2024-12-15 08:30 | 6365.2 | 99 | 2.62 | 25.92 | 2.16 | -0.1 | -1.44 | 28.44 | -1.57 | 103.16 | 0.45 | 16.74 | 54.7 | 103.14 | 64.29 | 26.85 | 33.08 | 8.51 | 2.72 | 1 | 5949.67 | 97.15 | 60.65 | 372.83 | 2520.56 | 6.9 | 3.62 | 103.56 | 15.8 | 3.28 | 2.66 | 103.26 | 3.72
2024-12-15 08:45 | 6373.2 | 99 | 2.62 | 26.6 | 2.16 | -0.1 | -1.51 | 28.47 | -1.53 | 103.15 | 0.45 | 16.63 | 54.82 | 103.14 | 64.33 | 26.76 | 32.78 | 8.51 | 2.72 | 1 | 5970.2 | 97.13 | 60.65 | 372.67 | 2505.06 | 6.9 | 3.61 | 103.52 | 15.79 | 3.29 | 2.64 | 103.25 | 3.71
2024-12-15 09:00 | 6381.13 | 99 | 2.61 | 26.17 | 2.16 | -0.09 | -1.56 | 28.5 | -1.7 | 103.14 | 0.45 | 16.62 | 54.8 | 103.14 | 64.37 | 26.71 | 32.94 | 8.51 | 2.72 | 1 | 5985.6 | 97.1 | 60.65 | 372.52 | 2518.7 | 6.91 | 3.63 | 103.48 | 15.77 | 3.28 | 2.63 | 103.23 | 3.72
2024-12-15 09:15 | 6385.8 | 99 | 2.62 | 25.65 | 2.16 | -0.08 | -1.5 | 28.46 | -1.6 | 103.13 | 0.45 | 16.56 | 54.71 | 103.14 | 64.41 | 27.07 | 33.17 | 8.51 | 2.71 | 1 | 5968.65 | 97.08 | 60.65 | 372.36 | 2518.15 | 6.92 | 3.65 | 103.43 | 15.75 | 3.27 | 2.64 | 103.21 | 3.73
2024-12-15 09:30 | 6377.62 | 99 | 2.63 | 26.09 | 2.16 | -0.08 | -1.51 | 28.42 | -1.52 | 103.12 | 0.45 | 16.52 | 54.81 | 103.14 | 64.45 | 27.1 | 33.08 | 8.5 | 2.71 | 1 | 5980.31 | 97.06 | 60.66 | 372.21 | 2521.3 | 6.96 | 3.69 | 103.39 | 15.73 | 3.27 | 2.63 | 103.2 | 3.77
2024-12-15 09:45 | 6362.52 | 99 | 2.62 | 25.96 | 2.16 | -0.07 | -1.48 | 28.38 | -1.5 | 103.1 | 0.45 | 16.48 | 54.87 | 103.14 | 64.5 | 26.72 | 32.98 | 8.5 | 2.71 | 1 | 5958.39 | 97.03 | 60.66 | 372.05 | 2509.31 | 6.99 | 3.68 | 103.35 | 15.71 | 3.31 | 2.64 | 103.17 | 3.75
2024-12-15 10:00 | 6343.52 | 99 | 2.65 | 26.56 | 2.16 | -0.07 | -1.49 | 28.03 | -1.6 | 102.88 | 0.45 | 16.58 | 54.77 | 103.14 | 64.54 | 26.89 | 32.61 | 8.48 | 2.71 | 1 | 5867.8 | 97.01 | 60.66 | 371.96 | 2519.21 | 6.92 | 3.62 | 103.32 | 15.7 | 3.3 | 2.68 | 102.95 | 3.69
2024-12-15 10:15 | 6325.27 | 99 | 2.63 | 26.23 | 2.16 | -0.07 | -1.58 | 28.27 | -1.7 | 102.92 | 0.45 | 16.78 | 54.73 | 103.14 | 64.58 | 26.8 | 32.65 | 8.49 | 2.71 | 1 | 5943.38 | 96.99 | 60.66 | 372.01 | 2511.53 | 6.9 | 3.62 | 103.34 | 15.69 | 3.28 | 2.64 | 102.99 | 3.69
2024-12-15 10:30 | 6335.68 | 99 | 2.65 | 26.35 | 2.16 | -0.08 | -1.36 | 28.19 | -1.42 | 103.07 | 0.45 | 16.38 | 54.6 | 103.14 | 64.62 | 27.02 | 32.63 | 8.5 | 2.71 | 1 | 5891.38 | 96.96 | 60.66 | 372.05 | 2505.85 | 6.9 | 3.61 | 103.35 | 15.68 | 3.29 | 2.66 | 103.15 | 3.69
2024-12-15 10:45 | 6324.8 | 99 | 2.63 | 26.4 | 2.16 | -0.09 | -1.53 | 28.43 | -1.62 | 103.28 | 0.45 | 16.74 | 54.73 | 103.14 | 64.66 | 26.79 | 32.51 | 8.53 | 2.71 | 1 | 5947.82 | 96.94 | 60.66 | 372.1 | 2525.79 | 6.91 | 3.61 | 103.36 | 15.67 | 3.3 | 2.64 | 103.37 | 3.7
2024-12-15 11:00 | 6395.32 | 99 | 2.61 | 25.76 | 2.16 | -0.1 | -1.57 | 28.72 | -1.7 | 103.9 | 0.45 | 16.65 | 54.74 | 103.14 | 64.7 | 27.08 | 33.37 | 8.58 | 2.71 | 1 | 6028.39 | 96.91 | 60.66 | 372.14 | 2536.73 | 6.93 | 3.66 | 103.37 | 15.66 | 3.27 | 2.6 | 104 | 3.76
2024-12-15 11:15 | 6408.52 | 99 | 2.58 | 25.43 | 2.16 | -0.09 | -1.55 | 28.74 | -1.63 | 103.96 | 0.45 | 16.66 | 54.81 | 103.14 | 64.74 | 27.06 | 33.46 | 8.58 | 2.71 | 1 | 6069.33 | 96.89 | 60.66 | 372.19 | 2533.24 | 6.98 | 3.7 | 103.39 | 15.66 | 3.28 | 2.58 | 104.05 | 3.79
2024-12-15 11:30 | 6428.95 | 99 | 2.59 | 25.97 | 2.16 | -0.1 | -1.72 | 28.84 | -1.81 | 104.01 | 0.45 | 16.69 | 54.82 | 103.14 | 64.79 | 26.67 | 33.24 | 8.57 | 2.71 | 1 | 6067.37 | 96.87 | 60.66 | 372.24 | 2518.86 | 7.04 | 3.7 | 103.4 | 15.65 | 3.34 | 2.58 | 104.11 | 3.8
2024-12-15 11:45 | 6427.68 | 99 | 2.59 | 25.78 | 2.16 | -0.11 | -1.48 | 28.86 | -1.54 | 104.07 | 0.45 | 16.6 | 54.82 | 103.14 | 64.83 | 26.7 | 33.19 | 8.57 | 2.71 | 1 | 6031.26 | 96.84 | 60.64 | 372.28 | 2509.09 | 6.91 | 3.64 | 103.41 | 15.65 | 3.27 | 2.59 | 104.18 | 3.75
2024-12-15 12:00 | 6454.25 | 99 | 2.59 | 25.67 | 2.16 | -0.11 | -1.6 | 28.81 | -1.73 | 104.12 | 0.45 | 16.59 | 54.85 | 103.14 | 64.87 | 26.52 | 33.26 | 8.57 | 2.71 | 1 | 6029.56 | 96.8 | 60.5 | 372.33 | 2543.79 | 6.91 | 3.65 | 103.43 | 15.69 | 3.26 | 2.6 | 104.23 | 3.76
2024-12-15 12:15 | 6463.55 | 99 | 2.6 | 25.25 | 2.16 | -0.11 | -1.5 | 28.9 | -1.55 | 104.18 | 0.45 | 16.69 | 54.95 | 103.14 | 64.91 | 26.96 | 33.55 | 8.57 | 2.71 | 1 | 6081.42 | 96.77 | 60.35 | 373.7 | 2489.2 | 7.02 | 3.75 | 103.81 | 15.8 | 3.27 | 2.6 | 104.29 | 3.86